## Sheet1
SSABT SETPOINT MODBUS ADDRESS TABLE
Baudrate : 115200
SETPOINT ID : 200
Index | Size | Description | Unit | Default | Range | Note
0 | WORD
1 | WORD
2 | WORD
3 | WORD
4 | WORD | Overvoltage Line to Line | Vrms | 4940 |  | 나누기 10
5 | WORD | Overvoltage Hysteresis | Vrms | 140 |  | 나누기 10
6 | WORD | In Phase Transfer Line to Line | Vrms | 3720 |  | 나누기 10
7 | WORD | In Phase Transfer Hysteresis | Vrms | 140 |  | 나누기 10
8 | WORD | Random Transfer Line To Line | Vrms | 3500 |  | 나누기 10
9 | WORD | Random Transfer Hysteresis | Vrms | 140 |  | 나누기 10
10 | WORD | Pickup Voltage Line to Line | Vrms | 4040 |  | 나누기 10
11 | WORD | Pickup Voltage Hysteresis | Vrms | 140 |  | 나누기 10
12 | WORD | Overload Average | Amp | 4610 |  | 나누기 10
13 | WORD | Overload Peak | Amp | 9750 |  | 나누기 10
14 | WORD | Phase Error | Degree | 600 |  | 나누기 10
15 | WORD | Time to Transfer Delay | ms | 0
16 | WORD | Re-Transfer Time (H) |  | 0
17 | WORD | Re-Transfer Time (L) | ms | 0
18 | WORD | Load Shed Time (H) |  | 10000
19 | WORD | Load Shed Time (L) | second | --
20 | WORD | Over frequency Dropout | Hz | 620
21 | WORD | Over frequency Pickup | Hz | 605
22 | WORD | Under Frequency Dropout | Hz | 564
23 | WORD | Under Frequency Pickup | Hz | 580
24
25
26
27
28
29